## Summary
Site Solar Evaluation Summary
Site Use/Name | Address | Assessment | Score | PV Array Size | Estimated Cost | Estimated Cost | Annual PV | Annual Load | PV % of Load | Annual Electric Cost | Potential Annual Savings* | Savings per Kw | 20YR REVENUE/KW | 20yr Array Revenue | Possible IRA Rebate | Rebate Amount | Simple Payback | Notes
|  |  |  | (kW DC) | (@ $2.288/W) | (@ $3.13/W) | (kWh) | (kWh) | % | $ | $ |  |  |  | % | $ | (years)
Pump: Middle | 131 E 13th St | Initial | 86 | 1025 | 2345200 | 3208250 | 1339971 | 906692 | 147.8% | 143633.35 | 165297.3 | 161.2657 | 3225.3132 | 3305946 | 50% | 1172600 | 7.0939 | Assumes we can get domestic content and LMI neighborhood
|  | Revised | 75 | 805.6 | 1843212.8 | 2521528 | 955999 | 906692 | 105.4% | 143633.35 | 151444.3041 |  |  |  | 50% | 921606.4 | 6.0854
Pump: Bayview | 6300 Highland | Initial | 90 | 818 | 1871584 | 2560340 | 1065471 | 225048 | 473.4% | 38625.47 | 80646.62 | 98.59 | 1971.8 | 1612932.4 | 70% | 1310108.8 | 6.9622 | qualifies for 10% energy community stacker (w/ comm solar and domestic we could get 70%)
|  | Revised | 89 | 1043 | 2386384 | 3264590 | 1230878 | 225048 | 546.9% | 38625.47 | 88916.97 |  |  |  | 70% | 1670468.8 | 8.0515 | added $0.05/kWh PPA excess in potential annual savings
Reservoir: Lincoln Park | 2798 W 10th St | Initial | 79.5 | 838 | 1917344 | 2622940 | 1044841 | 0 | n/a | 0 | 52242.05 |  |  | 0 | 60% | 1150406.4 | 14.6805 | with community solar = domestic content and LMI economic benefit stackers
|  | Revised | 80 | 819 | 1873872 | 2563470 | 961468 | 0 | n/a | 0 | 48073.4 |  |  |  | 60% | 1124323.2 | 15.5918 | assumes $0.05/kWh PPA
Water Treatment Plant (Bldg) | 8141 Congdon Blvd | Initial | 66 | 126 | 288288 | 394380 | 157090 | 6489000 | 2.421% | 830735.61 | 20110.9966 | 159.6111 | 3192.2217 |  | 40% | 115315.2 | 8.6009
|  | Revised | 68 | 161 | 368368 | 503930 | 186339 | 6489000 | 2.872% | 830735.61 | 23855.5159 |  |  |  | 40% | 147347.2 | 9.265
Water Treatment Plant (Site) | 8141 Congdon Blvd | Initial | 71 | 1099 | 2514512 | 3439870 | 1441439 | 6489000 | 22.21% | 830735.61 | 184536.0929 | 167.9127 | 3358.2546 | 4092941.79 | 40% | 1005804.8 | 8.1757 | assumes that we get domestic content bonus
|  | Revised | 66 | 701 | 1603888 | 2194130 | 859199 | 6489000 | 13.24% | 830735.61 | 109996.4872 |  |  |  | 40% | 641555.2 | 8.7488
Police Headquarters | 2030 N Arlington Ave | Initial | 78 | 485 | 1109680 | 1518050 | 408361 | 624401 | 65.4% | 81547.55 | 53332.4563 | 109.9638 | 2199.2766 | 1066649.127 | 40% | 443872 | 12.4841 | assumes that we get domestic content bonus
|  | Revised | 68.5 | 409 | 935792 | 1280170 | 347982 | 624401 | 55.73% | 81547.55 | 45446.8836 |  |  |  | 40% | 374316.8 | 12.3545
Fire Hall 2 | 2627 W Superior St | Initial | 78 | 34 | 77792 | 106420 | 43410 | 50041 | 86.75% | 2454.82 | 2129.5285 | 62.6332 | 1252.6638 | 42590.5702 | 60% | 46675.2 | 14.6121 | qualifies for 10% energy community stacker (w/ LMI and domestic stackers)
|  | Revised | 71 | 22.5 | 51480 | 70425 | 24752 | 50041 | 49.46% | 2454.82 | 1214.2384 |  |  |  | 60% | 30888 | 16.9588
City Center West / Fire Hall 8 | 5830 Grand Ave | Initial | 74 | 166 | 379808 | 519580 | 210588 | 213664 | 98.56% | 28129.55 | 27724.5848 | 167.0156 | 3340.3114 | 554491.6949 | 60% | 227884.8 | 5.4797 | qualifies for 10% energy community stacker (w/ LMI and domestic stackers) (could we get 20% LMI econ. Benefit Stacker?)
|  | Revised | 70 | 104 | 237952 | 325520 | 114360 | 213664 | 53.52% | 28129.55 | 15055.8603 |  |  |  | 60% | 142771.2 | 6.3218
Morgan Park Community Center | 1302 88th Ave W | Initial | 88 | 30 | 68640 | 93900 | 38864 | 29116 | 133.5% | 4726.2 | 5213.6 | 173.7867 | 3475.7333 | 104272 | 50% | 34320 | 6.5828 | assumes that we get domestic and LMI stackers
|  | Revised | 89 | 31 | 70928 | 97030 | 33594 | 29116 | 115.4% | 4726.2 | 5453.0829 |  |  |  | 50% | 35464 | 6.5035
Gary-New Duluth Community Center | 817 101st Ave W | Initial | 78.5 | 6 | 13728 | 18780 | 5784 | 4820 | 120% | 830.67 | 996.804 |  |  | 0 | 40% | 5491.2 | 8.2632 | Assumes that we get domestic stacker. Annual load error corrected in revised #.
|  | Revised | 76.5 | 16.2 | 37065.6 | 50706 | 17611 | 14460 | 121.8% | 2492 | 2649.55 |  |  |  | 40% | 14826.24 | 8.3936
Customer Service (Property Mntce) | 520 Garfield Ave | Initial | 72 | 447 | 1022736 | 1399110 | 543452 | 402438 | 135% | 56815.39 | 63866.09 | 142.8772 | 2857.5432 | 1277321.8 | 60% | 613641.6 | 6.4055 | McKinstry Study says 116% of load available - pg 15 (10% energy community stacker) (LMI and domestic stackers as well)
|  | Revised | 78 | 427 | 976976 | 1336510 | 491239 | 402438 | 122.1% | 56815.39 | 61255.44 |  |  |  | 60% | 586185.6 | 6.3797
*assumes PV generation in excess of 120% of annual load purchased by utility for $0.05/kWh
|  |  |  | 4539.3 | 10385918.4 | 14208009 |  |  |  |  | 553361.7324
4.5 MW
scoring notes
consider +120% load metric
structural overhaul may need to be a negative score
5:12 pitch for roofs may be better than 6:12.

## Pump Middle
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
131 E. 13th St. | [5 empty] | 805.6 | 75 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5 |  | Instructions
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| Grid Accessibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  | x |  | 3
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  | x |  |  | 4.5 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Permitted/Accesory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  |  | x |  |  | 6
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  |  |  |  | x | 1.5
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  | x |  |  |  | 6
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility |  | x |  |  |  | 4
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | x |  |  |  |  | 10

## Pump Bayview
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
6300 Highland Ave | [5 empty] | 1043 | 89 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5 |  | Instructions
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| Grid Accessibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  | x |  |  | 4.5
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  | x |  |  |  | 6 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) | x |  |  |  |  | 10
|  | South | SW or SE | West | East | North
| Orientation | x |  |  |  |  | 5
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) | x |  |  |  |  | 7.5
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  | x |  |  |  | 6
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility |  | x |  |  |  | 4
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | x |  |  |  |  | 10

## Pump Lincoln Park
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
2798 W. 10th St. | [5 empty] | 819 | 80 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5 |  | Instructions
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| Grid Accesibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  | x |  | 3
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  | x |  |  | 4.5 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  | x |  |  |  | 8
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  |  | x |  |  | 4.5
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  | x |  |  |  | 6
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility |  | x |  |  |  | 4
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | x |  |  |  |  | 10

## Water Treatment Plant (site)
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
8140 Congdon Blvd | [5 empty] | 701 | 66 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access
| Grid Accessibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  | x |  | 3 |  | Instructions
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0 |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| SAIFI Score (x1.5) |  |  |  | x |  | 3
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning |  |  |  |  | x | -2
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  |  |  | x |  | 4
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope |  | x |  |  |  | 3
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) |  |  | x |  |  | 3
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands |  | x |  |  |  | 2.5
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage |  |  | x |  |  | 2
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | x |  |  |  |  | 7.5
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) |  | x |  |  |  | 6
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch | [5 empty] | 0
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) | [5 empty] | 0
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) | [5 empty] | 0
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility | [5 empty] | 0
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | [5 empty] | 0

## Water Treatment Plant (bldg)
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
8140 Congdon Blvd | [5 empty] | 161 | 68 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Instructions
| Grid Accessibility (x2) | x |  |  |  |  | 10 |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  | x |  | 3
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  |  | x |  | 3
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts) |  |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  |  |  | x |  | 4
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  | x |  |  |  | 6
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  | x |  |  |  | 6
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility |  | x |  |  |  | 4
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) |  |  |  |  | x | 2

## Police Headquarters
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
2030 N. Arlington Ave | [5 empty] | 409 | 68.5 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5 |  | Instructions
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| Grid Accessibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  | x |  | 3
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  | x |  |  | 4.5 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  |  |  | x |  | 4
|  | South | SW or SE | West | East | North
| Orientation | x |  |  |  |  | 5
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  | x |  |  |  | 6
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  |  |  | x |  | 3
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility | x |  |  |  |  | 5
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) |  |  |  |  | x | 2

## Fire Hall 2
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
2627 W. Superior St. | [5 empty] | 22.5 | 71 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access
| Grid Accessibility (x2) | x |  |  |  |  | 10 |  | Instructions
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50 |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| SAIDI Score (x1.5) |  |  |  | x |  | 3
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  | x |  |  | 4.5
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed |  |  | x |  |  | 3
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  | x |  |  |  | 8
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  |  | x |  |  | 4.5
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  | x |  |  |  | 6
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility | x |  |  |  |  | 5
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) |  |  |  |  | x | 2

## City Center West
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
5830 Grand Ave | [5 empty] | 104 | 70 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5 |  | Instructions
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| Grid Accessibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  |  | x | 1.5
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  |  | x |  | 3 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  | x |  |  |  | 8
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  |  | x |  |  | 4.5
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  | x |  |  |  | 6
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility | x |  |  |  |  | 5
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) |  |  |  |  | x | 2

## Morgan Park CC
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
1302 88th Ave W. | [5 empty] | 31 | 89 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access
| Grid Accessibility (x2) | x |  |  |  |  | 10 |  | Instructions
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50 |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| SAIDI Score (x1.5) | x |  |  |  |  | 7.5
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) | x |  |  |  |  | 7.5
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) |  |  | x |  |  | 6
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  |  | x |  |  | 6
|  | South | SW or SE | West | East | North
| Orientation | x |  |  |  |  | 5
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  | x |  |  | 3
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) | x |  |  |  |  | 7.5
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) | x |  |  |  |  | 7.5
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility |  | x |  |  |  | 4
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | x |  |  |  |  | 10

## Gary-New Duluth CC
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
801 102nd Ave W | [5 empty] | 16.2 | 76.5 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5 |  | Instructions
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
| Grid Accessibility (x2) | x |  |  |  |  | 10
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  | x |  |  |  | 6
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  | x |  |  |  | 6 |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts)
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed |  |  | x |  |  | 3
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI resiliency created
| Service Disruption/resilience (x2) |  |  | x |  |  | 6
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  |  |  | x |  | 4
|  | South | SW or SE | West | East | North
| Orientation | x |  |  |  |  | 5
Complete the section below if the site is vacant
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  | x |  | 2
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  |  |  | x |  | 3
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) | x |  |  |  |  | 7.5
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility |  | x |  |  |  | 4
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | x |  |  |  |  | 10

## Customer Service (Prop. Main.)
Property Address |  |  | PID(s) |  |  | Array Size Kw (DC) | Property Score | Maximum Possible
520 Garfield Ave | [5 empty] | 427 | 78 | 100
| Category (multiplier) | 5 Points (or as noted) | 4 Points (or as noted) | 3 Points (or as noted) | 2 Points (or as noted) | 1 Point (or as noted) | Category Score
Complete this section for every site evaluated
|  | City Owned | Tax Forfeit | Available/For Sale | Private | Conservation
| Ownership | x |  |  |  |  | 5
|  | Grid Access | Transformer upgrade/install | Line Extension | Line extension & Transformer | No Grid Access |  |  | Instructions
| Grid Accessibility (x2) | x |  |  |  |  | 10 |  | Mark an "x" in the box under the corresponding description of the property in each category. Only mark one "x" per category to ensure proper property score. Sheet will automatically populate score.
|  | 200+ | 151-200 | 101-150 | 51-100 | 0-50
| SAIDI Score (x1.5) |  |  |  | x |  | 3
|  | 2.00+ | 1.34-1.99 | 0.67-1.33 | 0.01-0.66 | 0
| SAIFI Score (x1.5) |  |  |  | x |  | 3
|  | Permitted/Accessory Use | Conditional Use (3 pts) | Potential Zoning Change (1 pt) | Not Permitted (0 pts) | Within Floodzone/Shoreland (-2 pts) |  |  | Green Categories must be scored on every site. Only score the Yellow categories if the site is vacant or the Blue section if the site is occupied. the Yellow and Blue sections should never be completed for the same site
| Zoning | x |  |  |  |  | 5
|  | None Needed/NAD | RAP/CCP Completed | HazMat Survey/Phase II | Phase I | Unknown
| Brownfield Work Needed | x |  |  |  |  | 5
|  | Critical Infrastructure |  | Community Shelter/Hub |  | No CI/resiliency created
| Service Disruption/resilience (x2) | x |  |  |  |  | 10
|  | 70% Rebate Possible | 60% Rebate Possible | 50% Rebate Possible | 40% Rebate Possible | 30% Rebate Possible
| IRA Funding (x2) |  | x |  |  |  | 8
|  | South | SW or SE | West | East | North
| Orientation |  | x |  |  |  | 4
Complete the section below if the site is vacant or Parking Lot
|  | 0%-2% | 2%-6% (3 pts) | 6%-10% (1 pt) | 10%-15% (0 pts) | > 15% (-2 pts)
| Average Slope | [5 empty] | 0
|  | Sandy/Loam |  | Silty/Clay |  | Bedrock
| Soils (majority of site) | [5 empty] | 0
|  | None in area | Site Adjacent (2.5 pts) | < 25% of site (0 pts) | 25%-50% of site (-1 pts) | > 50% of site (-3 pts)
| Wetlands | [5 empty] | 0
|  | No Trees | Brush (3 pts) | Saplings Only (2 pts) | Mature Trees (0 pts) | Heavily Wooded (-1)
| Foliage | [5 empty] | 0
|  | 2 Entry Points for heavy equipment | 1 Entry Point For heavy equipment | 2 small/dirt hevicle entrances | 1 small/dirt vehicle entrance | Access to site must be built (-1 pt)
| Accessibility (x1.5) | [5 empty] | 0
|  | > 1 MW System | 500 Kw - 1 MW System | 250 Kw - 500 Kw System | 100 Kw - 250 Kw System | < 100 Kw System
| Solar System Size (x1.5) | [5 empty] | 0
Complete the section below if the site is occupied by a structure
|  | > 6-12 Pitch | 5-12 Pitch | 4-12 Pitch | 3-12 Pitch | Flat Roof
| Roof Pitch |  |  |  |  | x | 1
|  | Solar Ready | Roof good but need conduit | Roof Replacement | Structural Repairs | Complete Overhaul
| Structural Feasibility (x1.5) |  | x |  |  |  | 6
|  | No Obstructions | 1-2 Obstructions | 3-4 Obstructions | 5+Obstructions | no space
| Rooftop Obstructions (x1.5) |  |  |  | x |  | 3
|  | Heavy equipment/Internal Access | Heavy equipment/exterior access | Heavy equipment access only | Access with no heavy equipment | No access
| Accessibility | x |  |  |  |  | 5
|  | 100-120% capacity | 90%-100% capacity | 80%-89% capacity | 70%-79% capacity | < 70% capacity
| % of Load Capability (x2) | x |  |  |  |  | 10